## Basis
Item | Value
Plant at full load | 1000 kW, 881 kvar, pf 0.750
Drives (six-pulse, 3 % reactor) | 450 kW
Short-circuit level at 415 V | 23.9 MVA
kvar to reach pf 0.99 at full load | 738 kvar
Parallel resonance with plain capacitors | h = sqrt(Ssc / Qc): 200 kvar -> 10.92, 400 kvar -> 7.72, 725 kvar -> 5.74

## Harmonics
Configuration | Compensation (kvar) | Displacement pf | True pf | THDv 415 V (%) | Worst Vh 415 V (%) | TDD 415 V (%) | Isc/IL 415 V | TDD limit 415 V (%) | 415 V current OK | 415 V voltage OK | THDv 11 kV (%) | TDD 11 kV (%) | Isc/IL 11 kV | TDD limit 11 kV (%) | Caps within IEEE 18
A. Uncompensated | 0 | 0.75 | 0.746 | 3.96 | 2.83 | 11.23 | 17.9 | 5 | FALSE | TRUE | 0.27 | 11.23 | 263 | 15
B. Plain capacitor APFC | 750 | 0.992 | 0.917 | 9.38 | 7.77 | 41.16 | 23.7 | 8 | FALSE | FALSE | 0.64 | 41.16 | 347 | 15 | TRUE
C. Detuned APFC (7 %, 189 Hz) | 750 | 0.992 | 0.988 | 2.54 | 1.58 | 8.68 | 23.7 | 8 | FALSE | TRUE | 0.17 | 8.68 | 347 | 15 | TRUE
D. 5th + 7th tuned filters + detuned APFC | 750 | 0.992 | 0.99 | 1.78 | 0.99 | 5.41 | 23.7 | 8 | TRUE | TRUE | 0.12 | 5.41 | 347 | 15 | TRUE

## Capacitor duty
Configuration | Branch | V rms (%) | V peak (%) | I rms (%) | kvar (%) | Within limits
B. Plain capacitor APFC | Plain capacitors | 94.7 | 107.8 | 107.2 | 93.4 | TRUE
C. Detuned APFC (7 %, 189 Hz) | Detuned steps | 93 | 95.4 | 93.4 | 86.6 | TRUE
D. 5th + 7th tuned filters + detuned APFC | 5th filter (4.7) | 83 | 89.1 | 87.8 | 70.3 | TRUE
D. 5th + 7th tuned filters + detuned APFC | 7th filter (6.7) | 80.9 | 86.1 | 83.7 | 66.1 | TRUE
D. 5th + 7th tuned filters + detuned APFC | Detuned steps | 93 | 94.4 | 93.2 | 86.5 | TRUE

## Filter design
Branch | Effective kvar at 415 V | Tuned to | p = XL/XC (%) | C per phase, star (uF) | L per phase (mH) | R per phase (mOhm) | Capacitor voltage at 50 Hz (V) | Capacitor rating (V) | Nameplate kvar at rated V
Detuned step, 100 kvar | 100 | 3.78 (189 Hz) | 7 | 1718.8 | 0.4126 | 12.249 | 446 | 480 | 124
5th filter (4.7) | 300 | 4.70 (235 Hz) | 4.53 | 5293.7 | 0.0866 | 3.198 | 435 | 525 | 458
7th filter (6.7) | 150 | 6.70 (335 Hz) | 2.23 | 2710.6 | 0.0833 | 4.382 | 424 | 525 | 235

## 24 h APFC
Scheme | Switched steps (kvar) | Fixed filters (kvar) | kWh/day | kVAh/day without | kVAh/day with | kVAh saved (%) | Average pf without | Average pf with | Switching operations/day | Time below 0.98 (%)
C. Detuned APFC (7 %, 189 Hz) | 25 + 50 + 100 + 100 + 100 + 100 + 100 + 100 + 100 | 0 | 16817 | 23900 | 17032 | 28.7 | 0.704 | 0.987 | 41 | 3.8
D. 5th + 7th tuned filters + detuned APFC | 25 + 50 + 100 + 100 + 100 | 450 | 16817 | 23900 | 16990 | 28.9 | 0.704 | 0.99 | 117 | 3.1